Exhibit A - REVISED

Extension #1 (to 4/30/2022)

IUC Data Center/Virtualization RFP Response Analysis

In order to compare the various vendor RFP responses in a meaningful way for both physical and virtual datacenter options the following set of “typical” configurations (based on granulized real-world data and observations) and physical/temporal assumptions have been used to calculate per-rack costs:

Calculation Basis Assumptions

•	Typical Rack Footprint = 9 SQFT

•	Hours Per Typical Month = 720

•	In cases where respondents are not providing racks or PDUs for full rack configurations, a typical Rittal TS-8 42U rack ($1535.00) and two Rittal 9970750 208V/30A PDUs ($475.00 ea.) are included in the first year non-recurring costs

•	In cases where respondents are not providing racks or PDUs for half rack configurations, a typical Rittal TS-8 24U rack ($1430.00) and two APC AP7802 120V/30A PDUs ($642.00 ea.) are included in the first year non-recurring costs

•	In cases where respondents have not provided non-recurring installation costs for 208V/30A/3-Phase power, a scaling factor of 200% of 208V/20A is used to estimate costs – this factor was determined as a reasonable average of costs provided by the other respondents

•	In cases where respondents have not provided monthly recurring costs for 208V/30A/3-Phase power, a scaling factor of 70% of 208V/30A kW/h is used to estimate costs – this factor was determined as a reasonable average of costs provided by the other respondents

•	In cases where respondents have not provided a full set of installation or facility related non-recurring costs, a total value of $500.00 (less any actually defined costs) is used to estimate costs – this value was determined as a reasonable average of costs provided by the other respondents

•	In cases where respondents have not provided pricing for half rack (24U) options, a scaling factor of 60% of the full rack costs for non-power or facility related MRC/NRC is used to estimate costs – this value was determined as a reasonable average of costs provided by the other respondents

•	In cases where respondents have not provided non-recurring costs for OARnet connectivity to the first rack or virtual infrastructure, $150.00 is used to estimate costs – this value was determined as a reasonable average of costs provided by the other respondents

•	In cases where respondents have not provided monthly recurring costs for OARnet connectivity to the first rack or virtual infrastructure, $90.00 is used to estimated costs - this value was determined as a reasonable average of costs provided by the other respondents

Typical Fully Populated 42U Server Rack

•	A combination of 2U and 4U Dell/Sun servers

•	208 V/30 A A/B power feeds

•	Dual power supplies with one on each A/B feed

•	Balanced for less than 30 A total load to allow full function in event of loss of either A or B feed

•	Typical average load measured at 26 A (total across both feeds) - scaled to 5.4 kW/h for entire rack

Typical Fully Populated 24U Server Rack

•	A combination of 2U Dell/Sun servers

•	120 V/30 A A/B power feeds

•	Dual power supplies with one on each A/B feed

•	Balanced for less than 30 A total load to allow full function in event of loss of either A or B feed

•	Typical average load measured at 24 A (total across both feeds) - scaled to 3.1 kW/h for entire rack

Typical Fully Populated 42U Storage Rack

•	Aggregation of typical draw of EMC/Compellent storage processors and disk trays

•	208 V/30 A A/B power feeds

•	Dual power supplies with one on each A/B feed

•	Balanced for less than 30 A total load to allow full function in event of loss of either A or B feed

•	Typical average load measured at 22 A (total across both feeds) - scaled to 4.6 kW/h for entire rack

Typical 42U Server Rack with Blade Enclosure

•	A combination of up to 30U of 2U and 4U Dell/Sun servers, plus one fully loaded Dell M1000e Blade Enclosure

•	208 V/30 A/3-Phase A/B feeds for M1000e plus 208 V/30 A A/B power feeds for remaining systems

•	Dual power supplies with one on each A/B feed

•	Balanced for less that 30 A total load to allow full function in event of loss of wither A or B feed

•	Non-blade systems typical average load measured at 16 A (total across both feeds) - scaled to 3.3 kW/h for entire rack

•	Blade Enclosure typical average load measured at 14 A (total across both feeds and all phases) - scaled to 4.5 kW/h for entire rack

•	Total power estimate scaled to 7.8 kW/h combined

Typical Small Virtual Server

•	2 CPU

•	2 GB RAM

•	40 GB Tier-1 Storage

Typical Medium Virtual Server

•	2 CPU

•	4 GB RAM

•	80 GB Tier-1 Storage

Typical Large Virtual Server

•	2 CPU

•	8 GB RAM

•	120 GB Tier-1 Storage

## Executive Summary of Costs

The following data reflects the calculated costs for a single instance of each physical and virtual configuration identified above, and includes the cost of a single copper OARnet feed to the rack (which may be shared with subsequent racks) or OARnet presence availability within the virtual services infrastructure.

CBTS

These prices for physical do not include the purchase price of a cabinet or power strips in the cabinet.  We will allow customers to bring their own cabinets upon approval by the data center manager.  The OARnet fee reflects the on-net Cincinnati data center.  OARnet negotiated $50 cross connect per month for all OARnet clients.

Extra Large Virtual Server

•	4 CPU

•	16 GB RAM

•	300 GB Tier-1 Storage

•	Monitoring, Management and Patching included

Jumbo Virtual Server

•	4 CPU

•	32 GB RAM

•	500 GB Tier-1 Storage

•	Monitoring, Management and Patching included

|  | OPTION | FIRST YEAR TOTAL | SUBSEQUENT YEAR COST | THREE YEAR TOTAL | FIVE YEAR TOTAL |
| --- | --- | --- | --- | --- | --- |
|  | Typical Server Rack | $17,005.88 | $15,176.47 | $47,358.82 | $77,711.76 |
| PHYSICAL | Typical Storage Rack | $17,005.88 | $15,176.47 | $47,358.82 | $77,711.76 |
|  | Typical Blade Rack | $34,711.43 | $31,697.14 | $98,105.71 | $161,500.00 |
|  | Typical Half Rack | $12,714.29 | $11,057.14 | $34,828.57 | $56,942.86 |
|  | Small Virtual Machine | $1,473.60 | $1,473.60 | $4,420.80 | $7,368.00 |
|  | Medium Virtual Machine | $1,843.20 | $1,843.30 | $5,529.60 | $9,216.00 |
| VIRTUAL | Large Virtual Machine | $2,524.80 | $2,524.80 | $7,574.40 | $12,624.00 |
|  | Extra Large Virtual Machine | $5,191.20 | $5,191.20 | $15,573.60 | $25,956.00 |
|  | Jumbo Virtual Machine | $8,640.00 | $8,640.00 | $25,920.00 | $43,200.00 |
| Single OARnet feed (required by all above) | $850.00 | $600.00 | $2,050.00 | $3,250.00 |
|  | CBTS |  |  |  |  |
|  | OPTION | MRC –Storage Cost |
| STaaS | Storage as a Service* | .13/GB |
| * Storage can be added to any Virtual Machine for listed price per GB. |

|  | CBTS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | OPTION | MRC -License Cost | MRC -Storage Cost |
| BaaS | Virtual Server Backup* | $10 / Virtual Machine | .06/GB |

* Backup MRC pricing includes licensing and price per GB for backed up data.

|  | CBTS |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | OPTION | MRC -Storage Cost | Install/Setup per Virtual Machine | Replica Virtual Machine MRC | Recovered Virtual Machine* |
| DRaaS | Virtual Server Backup** | .06/GB | $175 | $110 | Published VM Rates |

* Recovered Virtual Machine pricing is only applicable during a failover test or actual declaration of Disaster as Virtual Machines are recovered and is charged on a daily rate.

** MRC includes Licensing, Virtual Machine Replica and price per GB of replicated data.

| Datacenter.bz |
| --- |
|  | OPTION | FIRST YEAR TOTAL | SUBSEQUENT YEAR COST | THREE YEAR TOTAL | FIVE YEAR TOTAL |
|  | Typical Server Rack | $19,070.00 | $16,320.00 | $51,710.00 | $84,350.00 |
| PHYSICAL | Typical Storage Rack | $19,070.00 | $16,284.00 | $51,638.00 | $84,206.00 |
|  | Typical Blade Rack | $33,362.00 | $27,612.00 | $88,586.00 | 143,810.00 |
|  | Typical Half Rack * | $12,974.00 | $10,974.00 | $34,922.00 | $56,870.00 |
|  | Small Virtual Machine | N/A | N/A | N/A | N/A |
| VIRTUAL | Medium Virtual Machine | N/A | N/A | N/A | N/A |
|  | Large Virtual Machine | N/A | N/A | N/A | N/A |
| Single OARNet feed (required by all above) | $3,250.00 | $3,000.00 | $9,250.00 | $15,250.00 |

Expedient

Physical -

| Colocation |  | Monthly Recurring Costs per Location |
| --- | --- | --- |
| Amp | Volt | Cleveland | Upper Arlington | Dublin |
| 20 | 120 | $ 453.42 | $ 355.63 | $ 442.18 |
| 30 | 120 | $ 680.14 | $ 533.45 | $ 663.26 |
| 20 | 208 | $ 785.80 | $ 616.35 | $ 766.64 |
| 30 | 208 | $ 1,178.70 | $ 924.52 | $ 1,149.94 |
| 50 | 208 | $ 1,964.50 | $ 1,540.87 | $ 1,916.58 |
| 30 | 3phase | $ 2,039.62 | $ 1,599.67 | $ 1,988.90 |

42U or 48U APC Cabinets and APC PDU's

Fully Redundant Power - A+B Power Whips and Breakers; Cold Isle Containment

Virtual -

Cloud - Generation Seven (7) Platform - all SSD Disk

- 20 Dell PowerEdge Servers: 2xE5-2650v4, 2.2GHz, 12 Core Processors, Intel 10Gb Base-T NIC, 384GB RAM per Server

- Juniper AFX5100-325 Switch Stack (Inter-POD Traffic), 4 Ports

- 2 - Juniper QFX5100-48T Switches, 10Gb Payload and Management Traffic

- 2 - Dell Compellent SC7020 SAN's, 30x3.84TB SSD Drives

- Total Generation 7 POD Virtual Colocation Capacity : 7TB RAM, 864vCPU, 480TB Disk

Expedient, cont.

| Cloud |  | Monthly Recurring Costs per Location are the same |
| --- | --- | --- |

Hosted Units of RAM - vSphere

Hosted Units of SSD Disk – vSphere

| Cost per unit of RAM | $ 12.00 |
| --- | --- |
| Cost per unit of Disk | $ 0.20 |
| Example: |  |  |
| 250GB of RAM | $ 3,000.00 |
| 1000GB of Disk | $ 200.00 |

Pricing includes vmWare, Microsoft OS and Linux OS licensing cost

Clients receive Virtual Center Access to their pool of resources (RAM, DISK, vCPU's)

Expedient also provides a DRaaS solution using Hypervisor-based Replication software: RPO (seconds)and RTO (minutes).